## Read-out data
| Read-out data |  | Version 2.2
Read-out data that can be parameterized
Data name | Type of data | Resolution | Number of Bytes
Identification of Parameter Set | INT6 | S0,S1,S2,S3,S4,S5 | 9
Active Energy Import Total | INT4 | 0.1 kWh | 6
Reactive Energy Import Total | INT4 | 0.1 kWh | 8
Active Energy Import Phase L1 Tarif 1 | INT4 | 0.1 kWh | 9
Active Energy Import Phase L2 Tarif 1 | INT4 | 0.1 kWh | 9
Active Energy Import Phase L3 Tarif 1 | INT4 | 0.1 kWh | 9
Active Energy Import Total Tarif 1 | INT4 | 0.1 kWh | 7
Active Energy Import Phase L1 Tarif 2 | INT4 | 0.1 kWh | 9
Active Energy Import Phase L2 Tarif 2 | INT4 | 0.1 kWh | 9
Active Energy Import Phase L3 Tarif 2 | INT4 | 0.1 kWh | 9
Active Energy Import Total Tarif 2 | INT4 | 0.1 kWh | 7
Active Energy Export Phase L1 Tarif 1 | INT4 | 0.1 kWh | 9
Active Energy Export Phase L2 Tarif 1 | INT4 | 0.1 kWh | 9
Active Energy Export Phase L3 Tarif 1 | INT4 | 0.1 kWh | 9
Active Energy Export Total Tarif 1 | INT4 | 0.1 kWh | 7
Active Energy Export Phase L1 Tarif 2 | INT4 | 0.1 kWh | 9
Active Energy Export Phase L2 Tarif 2 | INT4 | 0.1 kWh | 9
Active Energy Export Phase L3 Tarif 2 | INT4 | 0.1 kWh | 9
Active Energy Export Total Tarif 2 | INT4 | 0.1 kWh | 7
Reactive Energy Import Phase L1 Tarif 1 | INT4 | 0.1 kvarh | 10
Reactive Energy Import Phase L2 Tarif 1 | INT4 | 0.1 kvarh | 10
Reactive Energy Import Phase L3 Tarif 1 | INT4 | 0.1 kvarh | 10
Reactive Energy Import Total Tarif 1 | INT4 | 0.1 kvarh | 8
Reactive Energy Import Phase L1 Tarif 2 | INT4 | 0.1 kvarh | 10
Reactive Energy Import Phase L2 Tarif 2 | INT4 | 0.1 kvarh | 10
Reactive Energy Import Phase L3 Tarif 2 | INT4 | 0.1 kvarh | 10
Reactive Energy Import Total Tarif 2 | INT4 | 0.1 kvarh | 8
Reactive Energy Export Phase L1 Tarif 1 | INT4 | 0.1 kvarh | 10
Reactive Energy Export Phase L2 Tarif 1 | INT4 | 0.1 kvarh | 10
Reactive Energy Export Phase L3 Tarif 1 | INT4 | 0.1 kvarh | 10
Reactive Energy Export Total Tarif 1 | INT4 | 0.1 kvarh | 8
Reactive Energy Export Phase L1 Tarif 2 | INT4 | 0.1 kvarh | 10
Reactive Energy Export Phase L2 Tarif 2 | INT4 | 0.1 kvarh | 10
Reactive Energy Export Phase L3 Tarif 2 | INT4 | 0.1 kvarh | 10
Reactive Energy Export Total Tarif 2 | INT4 | 0.1 kvarh | 8
Active Power Phase L1 | INT4 | 0.001 kW | 8
Active Power Phase L2 | INT4 | 0.001 kW | 8
Active Power Phase L3 | INT4 | 0.001 kW | 8
Active Power Total | INT4 | 0.001 kW | 6
Reactive Power Phase L1 | INT4 | 0.001 kvar | 10
Reactive Power Phase L2 | INT4 | 0.001 kvar | 10
Reactive Power Phase L3 | INT4 | 0.001 kvar | 10
Reactive Power Total | INT4 | 0.001 kvar | 8
Tariff presently operating | INT1 | Tariff 1 or Tariff 2 | 4
Status Byte 4 (Range Overflow Alarms) | INT1 | - | 4
Apparent Power Phase L1 | INT4 | 0.001 kVA | 10
Apparent Power Phase L2 | INT4 | 0.001 kVA | 10
Apparent Power Phase L3 | INT4 | 0.001 kVA | 10
Apparent Power Total | INT4 | 0.001 kVA | 8
Voltage Phase L1 | INT2 | 0.1 V | 7
Voltage Phase L2 | INT2 | 0.1 V | 7
Voltage Phase L3 | INT2 | 0.1 V | 7
Voltage Total -> only single phase meter | INT2 | 0.1 V | (5)
Current Phase L1 | INT3 | 0.001 A | 8
Current Phase L2 | INT3 | 0.001 A | 8
Current Phase L3 | INT3 | 0.001 A | 8
Current Total | INT3 | 0.001 A | 6
Power factor cos φ Phase L1 | INT1 | 0.01 | 6
Power factor cos φ Phase L2 | INT1 | 0.01 | 6
Power factor cos φ Phase L3 | INT1 | 0.01 | 6
Power factor cos φ Total | INT1 | 0.01 | 4
Netfrequency | INT2 | 0.1 Hz | 5
Model | CHAR8 | 8 characters | 12
Total: 515*
* Warning: It’s possible to Read-out in one Telegram a maximum of 240 Bytes.

## Parameter Set for Read-out Data
| Parameter Set for Read-out Data |  |  |  |  | Version 2.2
Structure of Parameter Set for Read-out Data possible
The Parameter Set identification is an INT6 type (6 Bytes) => S0S1S2S3S4S5 <=
| S0 = Parameterset 0 | S1 = Parameterset 1 | S2 = Parameterset 2 | S3 = Parameterset 3 | S4 = Parameterset 4 | S5 = Parameterset 5
| value: 00 – 7F | value: 00 – FF | value: 00 – FF | value: 00 – FF | value: 00 – FF | value: 00 – FF
xxxx xxx1b | Parameterset Identification | Imported active or reactive energy phase L1 Tariff 1 | Exported active or reactive energy phase L1 Tariff 1 or Imported active or reactive energy phase L1 Tariff 1 | Active power phase L1 or Imported or exported reactive energy phase L1 Tariff 1 | Voltage Phase L1 -> By single phase meter is this the Voltage Total | Current Phase L1
xxxx xx1xb | Byte 4 State (Overflow Range Alarms) | Imported active or reactive energy phase L2 Tariff 1 | Exported active or reactive energy phase L2 Tariff 1 or Imported active or reactive energy phase L2 Tariff 1 | Active power phase L2 or Imported or exported reactive energy phase L2 Tariff 1 | Voltage Phase L2 | Current Phase L2
xxxx x1xxb | Parameterset 1 -> Instead of imported active energy -> Imported reactive energy | Imported active or reactive energy phase L3 Tariff 1 | Exported active or reactive energy phase L3 Tariff 1 or Imported active or reactive energy phase L3 Tariff 1 | Active power phase L3 or Imported or exported reactive energy phase L3 Tariff 1 | Voltage Phase L3 | Current Phase L3
xxxx 1xxxb | Parameterset 2 -> Instead of exported active energy -> Imported reactive energy | Total imported active or reactive energy Tariff 1 | Total exported active or reactive energy Tariff 1 or Total imported active or reactive energy Tariff 1 | Total active power or Total imported or exported reactive energy Tariff 1 | Active Energy Import Total | Total Current
xxx1 xxxxb | Parameterset 2 -> Instead of exported active energy -> Exported reactive energy | Imported active or reactive energy phase L1 Tariff 2 | Exported active or reactive energy phase L1 Tariff 2 or Imported active or reactive energy phase L1 Tariff 2 | Reactive or Apparent power phase L1 or Imported or exported reactive energy phase L1 Tariff 2 | Reactive Energy ImportTotal | Power factor cos phi Phase L1
xx1x xxxxb | Parameterset 3 -> Instead of active and reactive power -> Imported reactive power | Imported active or reactive energy phase L2 Tariff 2 | Exported active or reactive energy phase L2 Tariff 2 or Imported active or reactive energy phase L2 Tariff 2 | Reactive or Apparent power phase L2 or Imported or exported reactive energy phase L2 Tariff 2 | Reserve | Power factor cos phi Phase L2
x1xx xxxxb | Parameterset 3 -> Instead of active and reactive power -> Exported reactive power | Imported active or reactive energy phase L3 Tariff 2 | Exported active or reactive energy phase L3 Tariff 2 or Imported active or reactive energy phase L3 Tariff 2 | Reactive or Apparent power phase L3 or Imported or exported reactive energy phase L3 Tariff 2 | Netfrequency | Power factor cos phi Phase L3
1xxx xxxxb | Parameterset 3 -> Instead of reactive power -> Apparent power | Total imported active or reactive energy Tariff 2 | Total exported active or reactive energy Tariff 2 or Total imported active or reactive energy Tariff 2 | Total Reactive or Apparent power or Total imported or exported reactive energy Tariff 2 | Tariff presently operating | Total power factor cos phi
Default Parameter Set
These are set by the factory.
3 phase default Parameter Set Identification (INT6 Typ) = 09 FF 88 FF 9F 07
| S0 = Parameterset 0 | S1 = Parameterset 1 | S2 = Parameterset 2 | S3 = Parameterset 3 | S4 = Parameterset 4 | S5 = Parameterset 5
| value: 09 | value: FF | value: 88 | value: FF | value: 9F | value: 07
Default value | 0000 1001b | 1111 1111b | 1000 1000b | 1111 1111b | 1001 1111b | 0000 0111b
| Parameterset Identification Parameterset 2 Instead of exported active energy ->Imported reactive energy | Active - Energy Import Phase L1 Tariff 1 Active - Energy Import Phase L2 Tariff 1 Active - Energy Import Phase L3 Tariff 1 Active - Energy Import Total Tariff 1 Active - Energy Import Phase L1 Tariff 2 Active - Energy Import Phase L2 Tariff 2 Active - Energy Import Phase L3 Tariff 2 Active - Energy Import Total Tariff 2 | Total imported reactive energy Tariff 1 Total imported reactive energy Tariff 2 | Active - Power Phase L1 Active - Power Phase L2 Active - Power Phase L3 Active - Power Total Reactive - Power Phase L1 Reactive - Power Phase L2 Reactive - Power Phase L3 Reactive - Power Total | Voltage Phase L1 Voltage Phase L2 Voltage Phase L3 Active - Energy Import Total Reactive Energy Import Total Tariff presently operating | Current Phase L1 Current Phase L2 Current Phase L3
Total bytes | 9 | 68 | 16 | 68 | 39 | 24
single phase default Parameter Set Identification (INT6 Typ) = 0B 88 88 88 99 08
| S0 = Parameterset 0 | S1 = Parameterset 1 | S2 = Parameterset 2 | S3 = Parameterset 3 | S4 = Parameterset 4 | S5 = Parameterset 5
| value: 0B | value: 88 | value: 88 | value: 88 | value: 99 | value: 08
Default value | 0000 1011b | 1000 1000b | 1000 1000b | 1000 1000b | 1001 1001b | 0000 1000b
| Parameterset Identification Byte 4 State Parameterset 2 Instead of exported active energy ->Imported reactive energy | Active - Energy Import Total Tariff 1 Active - Energy Import Total Tariff 2 | Total imported reactive energy Tariff 1 Total imported reactive energy Tariff 2 | Active - Power Total Reactive - Power Total | Voltage Total Active - Energy Import Total Reactive Energy Import Total Tariff presently operating | Current Total
Total bytes | 13 | 14 | 16 | 14 | 23 | 6
Total: 3 phase energy meter = 224 Byte and single phase energy meter = 86 Byte.

## Primary and Secondary Address
| Primary and Secondary Address |  |  |  | Version 2.2
Primary Address (A-Field)
Field A (address field) contains the Primary Address of the M-Bus device and is used to identify the device.
Field A can have a value between 0 and 255.
Structure of Primary Address (A-Field)
A-Field (Hex) |  | Primary address | Description
0 |  | 0 | Factory setting
01 – FA |  | 1 - 250 | Settable primary addresses
FB, FC |  | 251, 252 | Reserved for future use
FD |  | 253 | Used to send information to all devices previously selected by secondary addresses
FE |  | 254 | Used to send information to all devices connected to the M-Bus network (Broadcast telegram). All the devices respond with a reception confirmation or with theirprimary address.
FF |  | 255 | Used to send information to all devices connected to the M-Bus network (Broadcast telegram). The telegrams with this addressing do not receive replies.
Secondary Address (UD)
If “FD” is set in A-field, the identification of the M-Bus device occurs on Secondary Address (UD):
Structure of Secondary Address (UD)
Identification number |  | Producer | Version | Medium
xxxxxxxx |  | mm mm | xx | 02
8-digit serial number of M-Bus device (secondary address) => 00000000 – 99999999 |  | 2 Byte constant | 1 Byte, firmware version => 01 - FF | 1 Byte, constant = electricity => 02
Wildcard
The M-Bus device reacts to the requests only if the constant parameters (manufacturer, version, medium)and the identification number coincide with those supplied.
"Wildcards" can be used in all 4 of these parameters.
The wildcard character is „F“.
Individual wildcards cannot be used for constant parameters.
Selection and Secondary Addressing When addressing in the network layer the address region is essentially extended beyond the number of 250 with primary addressing (A-Field). The addressing of the slaves takes place with secondary addressing with the help of the telegram ‘Select M-Bus device using Secondary Address(SND_UD)’ The master sends a SND_UD with the control information 52h to the address 253 (FDh) and fills the specific meter secondary address (identification number, manufacturer, version and medium) with the values of the slave which is to be addressed. The address FDh and the control information 52h are the indication for the slaves to compare the following secondary addresses with their own, and to change into the selected state should they agree. In this case the slave must answer the selection with an acknowledgement (E5h), otherwise the slave doesn’t send an answer. “Selected state” means that this slave will be addressed at the following commands (e.g. REQ_UD) with the bus address FDh and in this example will reply with RSP_UD. In other words the network layer has associated this slave with the address FDh. During selection individual positions of the secondary addresses can be occupied with wildcards (Fh). Such a Wildcard means that this position will not be taken account of during selection, and that the selection will be limited to specific positions, in order to address complete groups of slaves (Multicasting). In the identification number each individual digit can be wildcarded by a wildcard nibble Fh while the fields for manufacturer, version and medium can be wildcarded by a wildcard byte FFh. The state of the selection remains unchanged until the slave is deselected with a selection command (as described above) with non-matching secondary addresses, or a ‘Initialisation of M-Bus device(SND_NKE)’ telegram to address 253. A Slave also answers telegrams to his primary address.

## Telegrams Parameterization
Version 2.2
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | Comments
Reset M-Bus device access counter (SND_UD) | Value (Hex) | 68 | 03 | 03 | 68 | 73 | xx | 50 | xx | 16 | [10 empty] | This telegram resets the M-Bus device access counter, which is set at “0”. The M-Bus device confirms correct reception by means of a reply composed of a single character (ACK = E5). If the telegram is not received properly, the M-Bus device sends no confirmation.
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, Initialise the access counter (Set to „0“) | CS Checksum, calculated from C-Field to CI- Field incl. | Stop Character
Set baud rate (SND_UD) | Value (Hex) | 68 | 03 | 03 | 68 | 73 | xx | xx | xx | 16 | [10 empty] | This telegram sets the desired baud rate on the M-Bus device. The M-Bus device confirms correct reception by means of a reply composed of a single character (ACK = E5). If the telegram is not received properly, the M-Bus device sends no confirmation.The confirmation reply (ACK) is sent by the M-Bus device with the former baud rate. As soon as “ACK” is sent, the M-Bus device changes to the new baud rate that was set.
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, Set new Baudrate B8: 300 Baud B9: 600 Baud BA: 1200 Baud BB: 2400 Baud BC: 4800 Baud BD: 9600 Baud | CS Checksum, calculated from C-Field to CI- Field incl. | Stop Character
Set Parameter Set to Default Read-out Data (SND_UD) | Value (Hex) | 68 | 04 | 04 | 68 | 73 | xx | 51 | 7F | xx | 16 | [9 empty] | This Telegram sets the Parameter Set for the Read-out Data of the Default Parameter Set. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the Telegram has not been correctly received, the M- Bus device will not send an Acknowledgement.
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, Set Default Parameterset | CS Checksum, calculated from C-Field to DIF- Field incl. | Stop Character
Set Parameter Set to any Read-out Data desired (SND_UD) | Value (Hex) | 68 | 0C | 0C | 68 | 73 | xx | 51 | 06 | FD | 0B | "S0" | "S1" | "S2" | "S3" | "S4" | "S5" | xx | 16 |  | This Telegram sets the Parameter Set for Read-out Data of any value desired. For the Structure of the Parameter Set for Read-out Data please see: „Structure of Parameter Set for Read-out Data possible“. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement. | (1)Please see: Parameter Set of Read-out Data
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, 48 Bit Integer- Data (6 Byte) | VIF- Field, a standard VIFE follows | VIFE- Field, Std. VIFE = Parameterset- Identification | Parameter Set S0 (00 – FF) (1) | Parameter Set S1 (00 – FF) (1) | Parameter Set S2 (00 – FF) (1) | Parameter Set S3 (00 – FF) (1) | Parameter Set S4 (00 – FF) (1) | Parameter Set S5 (00 – FF) (1) | CS Checksum, calculated from C-Field to „S5“ incl. | Stop Character
Set Primary Address (SND_UD) | Value (Hex) | 68 | 06 | 06 | 68 | 73 | xx | 51 | 01 | 7A | xx | xx | 16 | [7 empty] | This Telegram sets a new Primary Address in the M-Bus device. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, 8 Bit Integer - Data (1 Byte) | VIF- Field, Set Primary Address | New Primary Address: Range: 00 – FA (0 – 250), Invalid : FB – FF (no action in meter) | CS Checksum, calculated from C-Field to Primary Address incl. | Stop Character
Set Secondary Address (SND_UD) | Value (Hex) | 68 | 09 | 09 | 68 | 73 | xx | 51 | 0C | 79 | xx | xx | xx | xx | xx | 16 |  |  |  |  | This Telegram sets a new Secondary Address in the M-Bus device. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement.
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, 8 digits BCD, 4 Byte | VIF- Field, Set Secondary Address | New Secondary Address digit 7 and 8, Range: 00 - 99 | New Secondary Address digit 5 and 6, Range: 00 - 99 | New Secondary Address digit 3 and 4, Range: 00 - 99 | New Secondary Address digit 1 and 2, Range: 00 - 99 | CS Checksum, calculated from C Field to Sec. Address incl. | Stop Character
Set Secondary Address and Manufacturer’s Mark (SND_UD) | Value (Hex) | 68 | 0D | 0D | 68 | 73 | xx | 51 | 07 | 79 | xx | xx | xx | xx | xx | xx | xx | xx | xx | 16 | This Telegram sets a new Secondary Address and a new Manufacturer’s Mark. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement.
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, 64 Bit Integer, 8 Byte | VIF- Field, Set Secondary Address and Manufacturer’s Mark | New Secondary Address digit 7 and 8, Range: 00 - 99 | New Secondary Address digit 5 and 6, Range: 00 - 99 | New Secondary Address digit 3 and 4, Range: 00 - 99 | New Secondary Address digit 1 and 2, Range: 00 - 99 | New Manufacturer’s Mark Byte 2, Range: 00 – FF | New Manufacturer’s Mark Byte 1, Range: 00 – FF | Version; This Parameter cannot be changed => Setting: Any Value 00 – FF | Medium; This Parameter is fixed to 02 and cannot be changed. => Setting: Any Value 00 - FF. | CS Checksum, calculated from C Field to Medium inclusive | Stop Character
Reset Active Energy Tariff 1 + 2 and Reactive Energy Tariff 1 + 2 (SND_UD) | Value (Hex) | 68 | 07 | 07 | 68 | 73 | xx | 51 | 01 | FF | 13 | xx | xx | 16 | [6 empty] | This Telegram enables to either Resetting the Active Energy Tariff 1 + 2 in the M-Bus device and/or to Resetting the Reactive Energy Tariff 1 + 2 (Set to “0”). The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement. Caution: This function is blocked in Electricity Meters with official certification (Metas or PTB Approval). | (2) Coding off Active and Reactive Energy Reset: 00h: No Reset Active and Reactive Energy (Binary: 0000 0000) 01h: Reset Active Energy (Binary: 0000 0001) 10h: Reset Reactive Energy (Binary: 0001 0000) 11h: Reset Reset Active and Reactive Energy (Binary: 0001 0001)
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, 8 Bit Integer (1 Byte) | VIF- Field, a manufacturer-specific VIFE follows | VIFE- Field, manufacturer-specific VIFE = Energy Reset | Coding off Active and Reactive Energy Reset (2) | CS Checksum, calculated from C-Field to Coding | Stop Character
Select M-Bus device using Secondary Address (SND_UD) | Value (Hex) | 68 | 0B | 0B | 68 | 73 | FD | 52 | "UD" | [7 empty] | xx | 16 |  |  | This Telegram selects M-Bus device. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5) and switch into Selection Mode. If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement. In Selection Mode the M-Bus device is ready to transmit the entire Read-out Data after receiving the Telegram „Transmit Read-out Data“ (Short Telegram REQ_UD2 with A- Field on FD). In Selection Mode the M-Bus device accepts also all telegrams with Primary Address on FD (A-Field on FD) The M-Bus device switch back to Normal Mode by receiving an invalid telegram or by receiving the telegram “ Initialisation of M-Bus device”
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Secondary Address | CI- Field, Selection of slave | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | CS Checksum, calculated from C-Field to Sekundary Address | Stop Character
Set Tariff (SND_UD) | Value (Hex) | 68 | 0B | 0B | 68 | 73 | xx | 51 | 02 | 7C | 03 | 72 | 61 | 74 | 00 | xx | xx | 16 |  |  | This Telegram sets a new operating Tariff in the M-Bus device. The M-Bus device confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus device will not send an Acknowledgement
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data send | DIF- Field, 16 Bit Integer - Data (2 Byte) | VIF- Field, VIF in following string (length in first byte) allows user definable VIF (in plain ASCII-String) | length of string | r' | a' | t' | DataHigh -> Always = '00' | DataLow --> 00 = Tariff1 01 = Tariff2 | CS Checksum, calculated from C-Field to DataLow incl. | Stop Character

## Transmit Read-out Data
| Transmit Read-out Data | [29 empty] | Version 2.2
Transmit Read-out Data (REQ_UD2)
The M-Bus device receives this Short Telegram and transmits the parametrized Read-out Data. The M-Bus device confirms correct receipt by transmitting of the Read-out Data. If the Short Telegram has not been received correctly, no Data will be transmitted by the M-Bus device. The Read-out Data are sent within 35 – 75 ms from receipt of the Short Telegram by the M-Bus device.
Byte Nr.
|  | 1 | 2 | 3 |  |  | 4 | 5
Transmit Read-out Data | Value (Hex) | 10 | 7B | xx |  |  | xx | 16
| Description | Start Character Short Telegram | C- Field, Transmit Read-out Data | A- Field, Primary Address 00 – FA : Valid Primary Address FB, FC : Reserved for future use FD : All M-Bus devices selectede via secondary address transmit the Read-out Data FE : All M-Bus devices in the System transmit the Read-out Data FF : No action by M-Bus device |  |  | CS Checksum, calculated from C-Field to A- Field | Stop Character
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | … | YY | YY+1 | YY+2 | YY+3 | YY+4 | YY+5 | … | YY+12 | YY+13 | YY+14
Telegram of Read-out Data by M-Bus device (RSP_UD) | Value (Hex) | 68 | xx | xx | 68 | 08 | xx | 72 | xxxxxxxx |  |  |  | xxxx |  | xx | 02 | xx | xx | 00 00 |  | 00 - EA |  |  | 0D | FC | 0C | 08 | xxxxxxxx |  |  | xx | 16
| Description | Start Character Long- Telegram | L- Field, number of bytes from C-Field to last byte of Model Code (YY+8) | L- Field Repetition | Start Character Long Telegram Repetition | C- Field, Transmit Data of M-Bus device | A- Field, Primary Address (00 – FA = 0 – 250) | CI- Field, Read-out Data of M-Bus device | 8-digit Secondary Address of M-Bus device |  |  |  | Manufacturer’s Mark |  | Version Number of M-Bus device Firmware (00 – FF) | Medium Electricity | Meter called upon, at each call on M-Bus device + 1 (00 – FF -> 00) | Shows the M-Bus device Status.(1) | Signature. For M-Bus device always on „0000“ |  | Read-out Data parametrised.(2) |  |  | DIF of Model Code | VIF of Model Code | VIFE of Model Code | Length of Model Code | Model Code = 8 characters |  |  | CS Check Sum, calculated from C Field to end of Model Code | Stop Character
The M-Bus slave always transmits the Model data to the Master, regardless of the Parameter Set
(1) Please see „Structure of Error Flags"
(2) Please see: ” Parameter Set for Read-out Data“
- Bytes No. 8 – 19 are the firm Data Record Header for every M-Bus device.
- Bytes No. 20 – YY are the Read-out Data defined in the Parameter Set.

## Telegram for Read-out Data
| Telegram for Read-out Data | [9 empty] | Version 2.2
The M-Bus device transmits Read-out Data to the Master depending on the Parameter Set. A summary of the options is shown under „ Parameterset for Read-out Data possible“.
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Parameterset Identification | Value (Hex) | 06 | FD | 0B | "S0" | "S1" | "S2" | "S3" | "S4" | "S5"
| Description | DIF, 48 Bit Integer, 6 Byte | VIF, followed by a Standart VIFE | Parameterset Identification | Parameterset S0 (00 – FF)(1) | Parameterset S1 (00 – FF)(1) | Parameterset S2 (00 – FF)(1) | Parameterset S3 (00 – FF)(1) | Parameterset S4 (00 – FF)(1) | Parameterset S5 (00 – FF)(1) |  |  |  | (1)Parameter Set for Read-out Data
Active Energy Import Total | Value (Hex) | Byte Nr. 1: 04; Byte Nr. 2: 05; Byte Nr. 3: xx; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Byte Nr. 2: VIF, Active Energy Total; Byte Nr. 3: Active Energy Import Total
Reactive Energy Import Total | Value (Hex) | 84 | 80 | 40 | 05 | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Register; Byte Nr. 4: VIF, Reactive Energy Total; Byte Nr. 5: Reactive Energy Import Total
Active Energy Import Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 10 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1; Byte Nr. 3: VIF, Active Energy, Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Active Energy Import Phase L1, L2 or L3
Active Energy Import Total Tariff 1 | Value (Hex) | Byte Nr. 1: 84; Byte Nr. 2: 10; Byte Nr. 3: 05; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx; Byte Nr. 7: xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1; Byte Nr. 3: VIF, Active Energy; Byte Nr. 4: Active Energy Import Total Tariff 1
Active Energy Import Phase L1 , L2 and L3 Tariff 2 | Value (Hex) | 84 | 20 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2; Byte Nr. 3: VIF, Active Energy, Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Active Energy Import Phase L1, L2 or L3
Active Energy Import Total Tariff 2 | Value (Hex) | Byte Nr. 1: 84; Byte Nr. 2: 20; Byte Nr. 3: 05; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx; Byte Nr. 7: xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2; Byte Nr. 3: VIF, Active Energy; Byte Nr. 4: Active Energy Import Total Tariff 2
Active Energy Export Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 10 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1; Byte Nr. 3: VIF, Active Energy, Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Active Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Active Energy Export Total Tariff 1 | Value (Hex) | Byte Nr. 1: 84; Byte Nr. 2: 10; Byte Nr. 3: 05; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx; Byte Nr. 7: xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1; Byte Nr. 3: VIF, Active Energy; Byte Nr. 4: Active Energy Export Total -> IntegerValue = Negative
Active Energy Export Phase L1, L2 and L3 Tariff 2 | Value (Hex) | 84 | 20 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2; Byte Nr. 3: VIF, Active Energy, Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Active Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Active Energy Export Total Tariff 2 | Value (Hex) | Byte Nr. 1: 84; Byte Nr. 2: 20; Byte Nr. 3: 05; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx; Byte Nr. 7: xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2; Byte Nr. 3: VIF, Active Energy; Byte Nr. 4: Active Energy Export Total -> IntegerValue = Negative
Reactive Energy Import Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 90 | 40 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Followed by a further VIFE; Byte Nr. 5: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 6: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 7: Reactive Energy Import Phase L1, L2 or L3
Reactive Energy Import Total Tariff 1 | Value (Hex) | 84 | 90 | 40 | 05 | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Byte Nr. 5: Reactive Energy Import Total
Reactive Energy Import Phase L1, L2 and L3 Tariff 2 | Value (Hex) | 84 | A0 | 40 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Followed by a further VIFE; Byte Nr. 5: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 6: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 7: Reactive Energy Import Phase L1, L2 or L3
Reactive Energy Import Total Tariff 2 | Value (Hex) | 84 | A0 | 40 | 05 | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Byte Nr. 5: Reactive Energy Import Total
Reactive Energy Export Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 90 | 40 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Followed by a further VIFE; Byte Nr. 5: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 6: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 7: Reactive Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Reactive Energy Export Total Tariff 1 | Value (Hex) | 84 | 90 | 40 | 05 | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 1 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Byte Nr. 5: Reactive Energy Export Total -> IntegerValue = Negative
Reactive Energy Export Phase L1, L2 and L3 Tariff 2 | Value (Hex) | 84 | A0 | 40 | 85 | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Followed by a further VIFE; Byte Nr. 5: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 6: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 7: Reactive Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Reactive Energy Export Total Tariff 2 | Value (Hex) | 84 | A0 | 40 | 05 | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Tariff 2 ; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Energy; Byte Nr. 5: Reactive Energy Export Total -> IntegerValue = Negative
Active Power Phase L1, L2 and L3 | Value (Hex) | 04 | AB | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Byte Nr. 2: VIF, Active Power; Followed by a further VIFE; Byte Nr. 3: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 4: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 5: Active Power Phase L1, L2 or L3
Active Power Total | Value (Hex) | Byte Nr. 1: 04; Byte Nr. 2: 2B; Byte Nr. 3: xx; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Byte Nr. 2: VIF, Active Power; Byte Nr. 3: Active Power Total
Reactive Power Phase L1, L2 and L3 | Value (Hex) | 84 | 80 | 40 | AB | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Total; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Power; Followed by a further VIFE; Byte Nr. 5: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 6: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 7: Reactive Power Phase L1, L2 or L3
Reactive Power Total | Value (Hex) | 84 | 80 | 40 | 2B | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Total; Followed by a further DIFE; Byte Nr. 3: DIFE, Reactive Value; Byte Nr. 4: VIF, Reactive Power; Byte Nr. 5: Reactive Power Total
Apparent Power Phase L1, L2 and L3 | Value (Hex) | 84 | C0 | 40 | AB | FF | 0x | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Total; Followed by a further DIFE; Byte Nr. 3: DIFE, Apparent Value; Byte Nr. 4: VIF, Apparent Power; Followed by a further VIFE; Byte Nr. 5: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 6: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 7: Apparent Power Phase L1, L2 or L3
Apparent Power Total | Value (Hex) | 84 | C0 | 40 | 2B | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE; Byte Nr. 2: DIFE, Total; Followed by a further DIFE; Byte Nr. 3: DIFE, Apparent Value; Byte Nr. 4: VIF, Apparent Power; Byte Nr. 5: Apparent Power Total
Voltage Phase L1, L2 and L3 | Value (Hex) | Byte Nr. 1: 02; Byte Nr. 2: FD; Byte Nr. 3: C8; Byte Nr. 4: FF; Byte Nr. 5: 0x; Byte Nr. 6: xx; Byte Nr. 7: xx
| Description | Byte Nr. 1: DIF, 16 Bit Integer, 2 Byte; Byte Nr. 2: VIF, Followed by a VIFE; Byte Nr. 3: VIFE = Voltage; Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Voltage Phase L1, L2 or L3
Voltage Total single Phase Meter | Value (Hex) | Byte Nr. 1: 02; Byte Nr. 2: FD; Byte Nr. 3: 48; Byte Nr. 4: xx; Byte Nr. 5: xx
| Description | Byte Nr. 1: DIF, 16 Bit Integer, 2 Byte; Byte Nr. 2: VIF, Followed by a VIFE; Byte Nr. 3: VIFE = Voltage; Byte Nr. 4: Voltage Total
Current Phase L1, L2 and L3 | Value (Hex) | 03 | FD | D9 | FF | 0x | xx | xx | xx
| Description | Byte Nr. 1: DIF, 23 Bit Integer, 3 Byte; Byte Nr. 2: VIF, Followed by a VIFE; Byte Nr. 3: VIFE = Current; Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Current Phase L1, L2 or L3
Current Total | Value (Hex) | Byte Nr. 1: 03; Byte Nr. 2: FD; Byte Nr. 3: 59; Byte Nr. 4: xx; Byte Nr. 5: xx; Byte Nr. 6: xx
| Description | Byte Nr. 1: DIF, 23 Bit Integer, 3 Byte; Byte Nr. 2: VIF, Followed by a VIFE; Byte Nr. 3: VIFE = Current Total; Byte Nr. 4: Current Total
Power factor cos phi Phase L1, L2 and L3 | Value (Hex) | Byte Nr. 1: 01; Byte Nr. 2: FF; Byte Nr. 3: E1; Byte Nr. 4: FF; Byte Nr. 5: 0x; Byte Nr. 6: xx
| Description | Byte Nr. 1: DIF, 8 Bit Integer, 1 Byte; Byte Nr. 2: VIF, Followed by an Manufacturer-spec.VIFE; Byte Nr. 3: Manufacturer-spec.VIFE = Power factor; Followed by a further VIFE; Byte Nr. 4: VIFE, Followed by an Manufacturer-spec.VIFE; Byte Nr. 5: Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3; Byte Nr. 6: Power factor cos phi Phase L1, L2 or L3
Power factor cos phi Total | Value (Hex) | Byte Nr. 1: 01; Byte Nr. 2: FF; Byte Nr. 3: 61; Byte Nr. 4: xx
| Description | Byte Nr. 1: DIF, 8 Bit Integer, 1 Byte; Byte Nr. 2: VIF, Followed by an Manufacturer-spec.VIFE; Byte Nr. 3: Manufacturer-spec.VIFE = Power factor cos phi; Byte Nr. 4: Power factor cos phi Total
Netfrequency | Value (Hex) | Byte Nr. 1: 02; Byte Nr. 2: FF; Byte Nr. 3: 52; Byte Nr. 4: xx; Byte Nr. 5: xx
| Description | Byte Nr. 1: DIF, 16 Bit Integer, 2 Byte; Byte Nr. 2: VIF, Followed by an Manufacturer-spec.VIFE; Byte Nr. 3: Manufacturer-spec.VIFE = Netfrequency; Byte Nr. 4: Netfrequency
Staus Byte 4 (Range Overflow) | Value (Hex) | Byte Nr. 1: 01; Byte Nr. 2: FD; Byte Nr. 3: 17; Byte Nr. 4: xx
| Description | Byte Nr. 1: DIF, 8 Bit Integer, 1 Byte; Byte Nr. 2: VIF, Followed by a VIFE; Byte Nr. 3: VIFE = Status (Error) Flags; Byte Nr. 4: Status Byte 4 (Range Overflow)
Tariff presently operating | Value (Hex) | Byte Nr. 1: 01; Byte Nr. 2: FF; Byte Nr. 3: 13; Byte Nr. 4: 0x
| Description | Byte Nr. 1: DIF, 8 Bit Integer, 1 Byte; Byte Nr. 2: VIF, Followed by an Manufacturer-spec.VIFE; Byte Nr. 3: Manufacturer-spec.VIFE = Tariff presently operating; Byte Nr. 4: Tariff presently operating 00: no connection to the Meter 01: Tariff 1 02 : Tariff 2
Model | Value (Hex) | 0D | FD | 0C | 08 | xx | xx | xx | xx | xx | xx | xx | xx
| Description | Byte Nr. 1: DIF, variable length; Byte Nr. 2: VIF, Followed by a VIFE; Byte Nr. 3: VIFE = Model; Byte Nr. 4: Length of data; Byte Nr. 5: Model Code = 8 characters

## Telegram of Error Flags
| Telegram of Error Flags | [9 empty] | Version 2.2
Telegram of Error Flags (REQ_UD1)
The Error Flags are transmitted by the M-Bus device within 35 – 75 ms from receipt of the Short Telegram „Transmit Error Flags“. Remark: The Error Flag and the M-Bus device Status on the Read-out Data Header are identical. The M-Bus device confirms correct receipt by Transmit the Error Flags. If there aren’t Error Flags set, the M-Bus device confirms correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram was not correctly received the M-Bus device will not send an Acknowledgement.
Byte Nr.
|  | 1 | 2 | 3 |  |  | 4 | 5
Transmit Error Flags of M-Bus device | Value (Hex) | 10 | 7A | xx |  |  | xx | 16
| Description | Start Character Short Telegram | C- Field. Transmit Error Flags | A Field, Primary Address 00 – FA : Valid Primary Address FB, FC : Reserved for future use FD : All M-Bus devices selectede via secondary address transmit the Read-out Data FE : All M-Bus device in the System send the Error Flags FF : No action by M-Bus device |  |  | CS Checksum, calculated from C-Field to A- Field incl. | Stop Character
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Telegram of Error Flags (RSP_UD) | Value (Hex) | 68 | 04 | 04 | 68 | 08 | xx | 71 | xx | xx | 16
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start Character Repetition | C- Field. Transmit Data from M-Bus device | A- Field, Primary Address (00 – FA = 0 – 250) | CI- Field, Error Flags of M-Bus device | Error Flags(1) | CS Checksum, calculated from C-Field to Error Flags incl. | Stop Character
(1) Please see „Structure of Error Flags" “
The Error Flags are transmitted by the M-Bus device within 35 – 75 ms from receipt of the Short Telegram „Transmit Error Flags of M-Bus device“.
Remark: If there aren’t Error Flags set, the M-Bus device confirms correct receipt by Single Character Acknowledgement (ACK = E5).

## Structure of Error Flags
| Structure of Error Flags |  | Version 2.2
Structure of Error Flags M-Bus device
The M-Bus device automatically carries out every second a number of internal tests, and, in the event of an Error, sets the corresponding Flag.
Error Flag (Binär) | Error Flag (Hex Value) | Description
xxxx 0000 | x0 | No Error set. => No Error in M-Bus device
xxxx 0001 | x1 | Error on Micro or Hardware fault.
xxxx 0010 | x2 | Overflow of internal Stack.
xxxx 0100 | x4 | Error on internal RAM (Memory Cell fault, etc..).
xxxx 1000 | x8 | Error on internal FLASH Memory.
xxxx 0011 | x3 | Error on Micro or Hardware fault and Overflow of internal Stack.
xxxx 0101 | x5 | Error on Micro or Hardware fault and Error on internal RAM.
xxxx 0110 | x6 | Overflow of internal Stack and Error on internal RAM.
xxxx 0111 | x7 | Error on Micro or Hardware fault and Overflow of internal Stack and Error on internal RAM.
xxxx 1001 | x9 | Error on Micro or Hardware fault and Error on internal FLASH Memory.
xxxx 1010 | xA | Overflow of internal Stack and Error on internal FLASH Memory.
xxxx 1011 | xB | Error on Micro or Hardware fault Overflow of internal Stack and Error on internal FLASH Memory.
xxxx 1100 | xC | Error on internal RAM and Error on internal FLASH Memory.
xxxx 1101 | xD | Error on Micro or Hardware fault and Error on internal RAM and Error on internal FLASH Memory.
xxxx 1110 | xE | Overflow of internal Stack and Error on internal RAM and Error on internal FLASH Memory.
xxxx 1111 | xF | Error on Micro or Hardware fault and Overflow of internal Stack and Error on internal RAM and Error on internal FLASH Memory.

## Initialisation of M-Bus
| Initialisation of M-Bus |  |  |  | Version 2.2
Initialisation of M-Bus device (SND_NKE)
This Short Telegram re-initialises the M-Bus device. The M-Bus device confirms correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram was not correctly received the M-Bus device will not send an Acknowledgement.
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5
Initialisation of M-Bus device | Value (Hex) | 10 | 40 | xx | xx | 16
| Description | Start Character Short Telegram | C- Field. REQ-UD2 | A Field, Primary Address 00 – FA : Valid Primary Address FB, FC : Reserved for future use FD : All M-Bus devices selectede via secondary address transmit the Read-out Data FE : All M-Bus device in the System send the ACK FF : No action by M-Bus device | CS Checksum, calculated from C-Field to A- Field | Stop Character